## Plant Info
Field | Value
Plant ID | BA558F95-8A3F-4769-9C78-FF7B6C639DDF
Plant Name | C2 CPP
FY | 2026-27
Month | 4
Year | 2026
Generated | 2026-06-30 18:42:59

## Assets
Asset ID | Asset Name | Display Name | Type | Plant Code | Utility Gen FK | Utility Dist FK
4EA0FA06-25BC-4A96-8279-2F4F4EC52E48 | JMD - C2-GTG 1 | GT-1 | GT | 36H0 | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9
63D052A9-9D13-4C59-B6CD-D26335C94E3B | JMD - C2-GTG 2 | GT-2 | GT | 36GX | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9
8021E7E4-B8FE-41F3-ACAB-F5F139DADBA3 | JMD - C2-STG 1 | STG-1 | STG | 36HM | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9

## Operational Hours
Asset | Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Total
JMD - C2-GTG 1 | GT | 2026-27 | 676 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 503 | 8475
JMD - C2-GTG 2 | GT | 2026-27 | 710 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 544 | 8550
JMD - C2-STG 1 | STG | 2026-27 | 0 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 440 | 7736

## Power Priority
Asset | Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar
JMD - C2-GTG 1 | GT | 2026-27 | 2 | 5 | 5 | 6 | 6 | 1 | 1 | 2 | 2 | 5 | 3 | 3
JMD - C2-GTG 2 | GT | 2026-27 | 1 | 1 | 4 | 2 | 5 | 3 | 6 | 1 | 4 | 2 | 5 | 2
JMD - C2-STG 1 | STG | 2026-27 | 1 | 1 | 4 | 2 | 5 | 3 | 6 | 1 | 4 | 2 | 7 | 3

## Steam Priority
Asset | Type | Steam Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar
AUXBOIL7_SHP STEAM | AUXBOILER | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
AUXBOIL8_SHP STEAM | AUXBOILER | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
HP Steam PRDS | PRDS | HP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG1_C2_LP STEAM | HRSG | LP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG1_C2_SHP STEAM | HRSG | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG2_C2_LP STEAM | HRSG | LP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG2_C2_SHP STEAM | HRSG | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
LP Steam PRDS | PRDS | LP Steam_Dis | 2026-27 | bar: Apr to Mar
MP Steam PRDS SHP | PRDS | MP Steam_Dis | 2026-27 | bar: Apr to Mar

## Demands
Parameter | Value
power_process | 62526309
lp_process | 18336
mp_process | 4617
hp_process | -12252
shp_process | 265383
air_process | 11292305
nitrogen_asu_process | 10794261
dm_process | 129256
cw1_process | 0
cw2_process | 0
cooling_water_process | 89343
raw_water_process | 0
utility_water_process | 5163
ret_steam_condensate_process | -154158
oxygen_process | 38907
effluent_process | 75601
power_fixed_kwh | 20341283
power_fixed | 20341.283
lp_fixed | 4745
mp_fixed | 7925
hp_fixed | 238
shp_fixed | 94290
air_fixed | 1327713
nitrogen_asu_fixed | 1952800
dm_fixed | 55713
cw1_fixed | 0
cw2_fixed | 0
cooling_water_fixed | 10872
raw_water_fixed | 0
utility_water_fixed | 1523650
ret_steam_condensate_fixed | 1512
oxygen_fixed | 0
effluent_fixed | 131760

## Import Power
Source | Capacity MW | Hours | MWh
TOTAL |  |  | 0

## Norms
No data

## U4U Summary
Utility Plant | Utility | UOM | Gen Qty | BPC Gen Qty | Gen Diff % | # Materials | Total U4U Qty | Materials Consumed
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | 3 | 485989.4 | SynGas(Unshift), Boiler Feed Water, Power_Dis
Boiler Feed Water | Boiler Feed Water | M3 | 326219.74 | 434662.43 | -24.95 | 3 | 2968599.6 | D M Water, LP Steam_Dis, Power_Dis
COMPRESED AIR_ASU | COMPRESED AIR_ASU | NM3 | 721572.02 | 731759.52 | -1.39 | 1 | 90196.5 | Power_Dis
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14148471.33 | 14348225.29 | -1.39 | 3 | 2881619.16 | COMPRESED AIR_ASU, COMPRESSED AIR, Power_Dis
Cooling Water | Cooling Water | KM3 | 101151.46 | 105543.15 | -4.16 | 4 | 22766637.94 | COMPRESSED AIR, Effluent Treated, Power_Dis, SWRO WATER
D M Water | D M Water | M3 | 478565.61 | 604780.6 | -20.87 | 4 | 1315662.99 | COMPRESSED AIR, NITROGEN_ASU, Power_Dis, SWRO WATER
Effluent Treated | Effluent Treated | M3 | 384375.53 | 608424.78 | -36.82 | 5 | 2092623.82 | COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
HP Steam PRDS | HP Steam PRDS | MT | 17527.82 | 21910 | -20 | 2 | 17527.82 | Boiler Feed Water, SHP Steam_Dis
HP Steam_Dis | HP Steam_Dis | MT | 17527.83 | 21909.94 | -20 | 1 | 17527.83 | HP Steam PRDS
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | 3 | 521465.75 | SynGas(Unshift), Boiler Feed Water, Power_Dis
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | 3 | 545560.36 | SynGas(Unshift), Boiler Feed Water, Power_Dis
JMD - C2-GTG 1 | POWERGEN | KWH | 54080000 | 75215499.08 | -28.1 | 6 | 469847.04 | SynGas(Unshift), COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
JMD - C2-GTG 2 | POWERGEN | KWH | 77997310 | 47632624.3 | 63.75 | 6 | 686766.31 | SynGas(Unshift), COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
LP Steam PRDS | LP Steam PRDS | MT | 20468.45 | 25618.73 | -20.1 | 2 | 20468.45 | Boiler Feed Water, MP Steam_Dis
LP Steam_Dis | LP Steam_Dis | MT | 55702.85 | 69718.67 | -20.1 | 3 | 55702.85 | HRSG1_C2_LP STEAM, HRSG2_C2_LP STEAM, LP Steam PRDS
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 32824.59 | 37693.6 | -12.92 | 2 | 32824.59 | Boiler Feed Water, HP Steam_Dis
MP Steam_Dis | MP Steam_Dis | MT | 32824.59 | 37693.55 | -12.92 | 1 | 32824.59 | MP Steam PRDS SHP
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13270040.38 | 13335714.29 | -0.49 | 4 | 6314017.91 | MP Steam_Dis, Power_Dis, Ret steam condensate, Utility Water
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | 4 | 14623157.04 | MP Steam_Dis, Power_Dis, Ret steam condensate, Utility Water
SHP Steam_Dis | SHP Steam_Dis | MT | 376078.7 | 380180.38 | -1.08 | 3 | 376078.7 | AUXBOIL7_SHP STEAM, HRSG1_C2_SHP STEAM, HRSG2_C2_SHP STEAM
Utility Water | Utility Water | M3 | 1611316.04 | 256859.88 | 527.31 | 2 | 2122731.64 | COMPRESSED AIR, SWRO WATER
TOTAL |  |  | 163995463.93 | 154287905.87 |  | 65 | 58437830.31

## U4U Consumption
Utility Plant | Utility | UOM | Gen Qty | BPC Gen Qty | Gen Diff % | Account | Material | Material UOM | Norm | Quantity | BPC Quantity | Qty Diff %
JMD - C2-GTG 1 | POWERGEN | KWH | 54080000 | 75215499.08 | -28.1 | Raw Material | SynGas(Unshift) | MMBTU | 0.004368 | 236221.44 | 328541.3 | -28.1
JMD - C2-GTG 1 | POWERGEN | KWH | 54080000 | 75215499.08 | -28.1 | Utilities | COMPRESSED AIR | NM3 | 0.00128 | 69222.4 | 96268.87 | -28.09
JMD - C2-GTG 1 | POWERGEN | KWH | 54080000 | 75215499.08 | -28.1 | Utilities | Cooling Water | KM3 | 7e-06 | 378.56 | 496.39 | -23.74
JMD - C2-GTG 1 | POWERGEN | KWH | 54080000 | 75215499.08 | -28.1 | Utilities | NITROGEN_ASU | NM3 | 0.00166 | 89772.8 | 124848.69 | -28.09
JMD - C2-GTG 1 | POWERGEN | KWH | 54080000 | 75215499.08 | -28.1 | Utilities | Power_Dis | KWH | 0.00135 | 73008 | 101533.57 | -28.09
JMD - C2-GTG 1 | POWERGEN | KWH | 54080000 | 75215499.08 | -28.1 | Utilities | Utility Water | M3 | 2.3e-05 | 1243.84 | 1744.87 | -28.71
JMD - C2-GTG 2 | POWERGEN | KWH | 77997310 | 47632624.3 | 63.75 | Raw Material | SynGas(Unshift) | MMBTU | 0.004485 | 349817.94 | 213632.32 | 63.75
JMD - C2-GTG 2 | POWERGEN | KWH | 77997310 | 47632624.3 | 63.75 | Utilities | COMPRESSED AIR | NM3 | 0.00128 | 99836.56 | 60970.28 | 63.75
JMD - C2-GTG 2 | POWERGEN | KWH | 77997310 | 47632624.3 | 63.75 | Utilities | Cooling Water | KM3 | 7e-06 | 545.98 | 314.38 | 73.67
JMD - C2-GTG 2 | POWERGEN | KWH | 77997310 | 47632624.3 | 63.75 | Utilities | NITROGEN_ASU | NM3 | 0.00166 | 129475.53 | 79070.84 | 63.75
JMD - C2-GTG 2 | POWERGEN | KWH | 77997310 | 47632624.3 | 63.75 | Utilities | Power_Dis | KWH | 0.00135 | 105296.37 | 64304.6 | 63.75
JMD - C2-GTG 2 | POWERGEN | KWH | 77997310 | 47632624.3 | 63.75 | Utilities | Utility Water | M3 | 2.3e-05 | 1793.94 | 1105.09 | 62.33
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | Raw Material | SynGas(Unshift) | MMBTU | 2.8762 | 180684.2 | 247872.88 | -27.11
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | Utilities | Boiler Feed Water | M3 | 1.01 | 63448.2 | 87041.85 | -27.11
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | Utilities | Power_Dis | KWH | 3.85 | 241857 | 331793.2 | -27.11
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | Raw Material | SynGas(Unshift) | MMBTU | 3.3762 | 365174.55 | 607724.26 | -39.91
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | Utilities | Boiler Feed Water | M3 | 1.16 | 125465.6 | 208800.13 | -39.91
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | Utilities | Power_Dis | KWH | 0.285 | 30825.6 | 51300.03 | -39.91
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | Raw Material | SynGas(Unshift) | MMBTU | 3.3575 | 381408.36 | 382750.85 | -0.35
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | Utilities | Boiler Feed Water | M3 | 1.16 | 131776 | 132239.82 | -0.35
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | Utilities | Power_Dis | KWH | 0.285 | 32376 | 32489.96 | -0.35
Boiler Feed Water | Boiler Feed Water | M3 | 326219.74 | 434662.43 | -24.95 | Utilities | D M Water | M3 | 0.9 | 293597.76 | 391196.19 | -24.95
Boiler Feed Water | Boiler Feed Water | M3 | 326219.74 | 434662.43 | -24.95 | Utilities | LP Steam_Dis | MT | 0.1 | 32621.97 | 43466.24 | -24.95
Boiler Feed Water | Boiler Feed Water | M3 | 326219.74 | 434662.43 | -24.95 | Utilities | Power_Dis | KWH | 8.1 | 2642379.86 | 3520765.68 | -24.95
COMPRESED AIR_ASU | COMPRESED AIR_ASU | NM3 | 721572.02 | 731759.52 | -1.39 | Utilities | Power_Dis | KWH | 0.125 | 90196.5 | 91469.94 | -1.39
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14148471.33 | 14348225.29 | -1.39 | Utilities | COMPRESED AIR_ASU | NM3 | 0.051 | 721572.04 | 731759.49 | -1.39
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14148471.33 | 14348225.29 | -1.39 | Utilities | COMPRESSED AIR | NM3 | 0.00267 | 37776.42 | 38309.76 | -1.39
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14148471.33 | 14348225.29 | -1.39 | Utilities | Power_Dis | KWH | 0.15 | 2122270.7 | 2152233.79 | -1.39
Cooling Water | Cooling Water | KM3 | 101151.46 | 105543.15 | -4.16 | Utilities | COMPRESSED AIR | NM3 | 0.97474 | 98596.47 | 102877.24 | -4.16
Cooling Water | Cooling Water | KM3 | 101151.46 | 105543.15 | -4.16 | Utilities | Effluent Treated | M3 | 3.8 | 384375.54 | 401063.99 | -4.16
Cooling Water | Cooling Water | KM3 | 101151.46 | 105543.15 | -4.16 | Utilities | Power_Dis | KWH | 210.9 | 21332842.24 | 22259051.62 | -4.16
Cooling Water | Cooling Water | KM3 | 101151.46 | 105543.15 | -4.16 | Utilities | SWRO WATER | M3 | 9.4 | 950823.69 | 992105.67 | -4.16
D M Water | D M Water | M3 | 478565.61 | 604780.6 | -20.87 | Utilities | COMPRESSED AIR | NM3 | 0.04918 | 23535.86 | 29743.11 | -20.87
D M Water | D M Water | M3 | 478565.61 | 604780.6 | -20.87 | Utilities | NITROGEN_ASU | NM3 | 0.63 | 301496.33 | 381011.83 | -20.87
D M Water | D M Water | M3 | 478565.61 | 604780.6 | -20.87 | Utilities | Power_Dis | KWH | 0.92 | 440280.36 | 556398.22 | -20.87
D M Water | D M Water | M3 | 478565.61 | 604780.6 | -20.87 | Utilities | SWRO WATER | M3 | 1.15 | 550350.45 | 695497.78 | -20.87
Effluent Treated | Effluent Treated | M3 | 384375.53 | 608424.78 | -36.82 | Utilities | COMPRESSED AIR | NM3 | 2.2093 | 849201.64 | 1344194.09 | -36.82
Effluent Treated | Effluent Treated | M3 | 384375.53 | 608424.78 | -36.82 | Utilities | Cooling Water | KM3 | 3.1e-05 | 11.92 | 19.1 | -37.61
Effluent Treated | Effluent Treated | M3 | 384375.53 | 608424.78 | -36.82 | Utilities | NITROGEN_ASU | NM3 | 0.005814 | 2234.76 | 3537.38 | -36.82
Effluent Treated | Effluent Treated | M3 | 384375.53 | 608424.78 | -36.82 | Utilities | Power_Dis | KWH | 3.2 | 1230001.71 | 1946959.31 | -36.82
Effluent Treated | Effluent Treated | M3 | 384375.53 | 608424.78 | -36.82 | Utilities | Utility Water | M3 | 0.02907 | 11173.8 | 17686.91 | -36.82
HP Steam PRDS | HP Steam PRDS | MT | 17527.82 | 21910 | -20 | Utilities | Boiler Feed Water | M3 | 0.064 | 1121.78 | 1402.24 | -20
HP Steam PRDS | HP Steam PRDS | MT | 17527.82 | 21910 | -20 | Utilities | SHP Steam_Dis | MT | 0.936 | 16406.04 | 20507.71 | -20
LP Steam PRDS | LP Steam PRDS | MT | 20468.45 | 25618.73 | -20.1 | Utilities | Boiler Feed Water | M3 | 0.055 | 1125.76 | 1409.03 | -20.1
LP Steam PRDS | LP Steam PRDS | MT | 20468.45 | 25618.73 | -20.1 | Utilities | MP Steam_Dis | MT | 0.945 | 19342.69 | 24209.64 | -20.1
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 32824.59 | 37693.6 | -12.92 | Utilities | Boiler Feed Water | M3 | 0.1 | 3282.46 | 3769.36 | -12.92
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 32824.59 | 37693.6 | -12.92 | Utilities | HP Steam_Dis | MT | 0.9 | 29542.13 | 33924.2 | -12.92
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13270040.38 | 13335714.29 | -0.49 | Utilities | MP Steam_Dis | MT | 2.1e-05 | 278.67 | 280.05 | -0.49
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13270040.38 | 13335714.29 | -0.49 | Utilities | Power_Dis | KWH | 0.47426 | 6293449.35 | 6324508.53 | -0.49
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13270040.38 | 13335714.29 | -0.49 | Utilities | Ret steam condensate | M3 | -1.1e-05 | -145.97 | -146.69 | -0.49
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13270040.38 | 13335714.29 | -0.49 | Utilities | Utility Water | M3 | 0.00154 | 20435.86 | 20536.72 | -0.49
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | MP Steam_Dis | MT | 0.017 | 661.42 | 661.43 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Power_Dis | KWH | 374.61 | 14574951.27 | 14575100.97 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Ret steam condensate | M3 | -0.008 | -311.26 | -311.26 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Utility Water | M3 | 1.23 | 47855.61 | 47856.1 | 0
Utility Water | Utility Water | M3 | 1611316.04 | 256859.88 | 527.31 | Utilities | COMPRESSED AIR | NM3 | 0.21739 | 350283.99 | 55838.77 | 527.31
Utility Water | Utility Water | M3 | 1611316.04 | 256859.88 | 527.31 | Utilities | SWRO WATER | M3 | 1.1 | 1772447.65 | 282545.86 | 527.31
HP Steam_Dis | HP Steam_Dis | MT | 17527.83 | 21909.94 | -20 | Utilities | HP Steam PRDS | MT | 1 | 17527.83 | 21909.94 | -20
LP Steam_Dis | LP Steam_Dis | MT | 55702.85 | 69718.67 | -20.1 | Utilities | HRSG1_C2_LP STEAM | MT | 0.38727 | 21572.1 | 27000.02 | -20.1
LP Steam_Dis | LP Steam_Dis | MT | 55702.85 | 69718.67 | -20.1 | Utilities | HRSG2_C2_LP STEAM | MT | 0.24527 | 13662.29 | 17099.98 | -20.1
LP Steam_Dis | LP Steam_Dis | MT | 55702.85 | 69718.67 | -20.1 | Utilities | LP Steam PRDS | MT | 0.36746 | 20468.46 | 25618.67 | -20.1
MP Steam_Dis | MP Steam_Dis | MT | 32824.59 | 37693.55 | -12.92 | Utilities | MP Steam PRDS SHP | MT | 1 | 32824.59 | 37693.55 | -12.92
SHP Steam_Dis | SHP Steam_Dis | MT | 376078.7 | 380180.38 | -1.08 | Utilities | AUXBOIL7_SHP STEAM | MT | 0.22668 | 85250.27 | 86180.05 | -1.08
SHP Steam_Dis | SHP Steam_Dis | MT | 376078.7 | 380180.38 | -1.08 | Utilities | HRSG1_C2_SHP STEAM | MT | 0.47346 | 178058.22 | 180000.12 | -1.08
SHP Steam_Dis | SHP Steam_Dis | MT | 376078.7 | 380180.38 | -1.08 | Utilities | HRSG2_C2_SHP STEAM | MT | 0.29986 | 112770.21 | 113999.85 | -1.08