## Plant Info
Field | Value
Plant ID | BA558F95-8A3F-4769-9C78-FF7B6C639DDF
Plant Name | C2 CPP
FY | 2026-27
Month | 4
Year | 2026
Generated | 2026-07-02 10:08:15

## Assets
Asset ID | Asset Name | Display Name | Type | Plant Code | Utility Gen FK | Utility Dist FK
4EA0FA06-25BC-4A96-8279-2F4F4EC52E48 | JMD - C2-GTG 1 | GT-1 | GT | 36H0 | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9
63D052A9-9D13-4C59-B6CD-D26335C94E3B | JMD - C2-GTG 2 | GT-2 | GT | 36GX | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9
8021E7E4-B8FE-41F3-ACAB-F5F139DADBA3 | JMD - C2-STG 1 | STG-1 | STG | 36HM | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9

## Operational Hours
Asset | Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Total
JMD - C2-GTG 1 | GT | 2026-27 | 676 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 503 | 8475
JMD - C2-GTG 2 | GT | 2026-27 | 710 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 544 | 8550
JMD - C2-STG 1 | STG | 2026-27 | 0 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 440 | 7736

## Power Priority
Asset | Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar
JMD - C2-GTG 1 | GT | 2026-27 | 1 | 5 | 5 | 6 | 6 | 1 | 1 | 2 | 2 | 5 | 3 | 3
JMD - C2-GTG 2 | GT | 2026-27 | 1 | 1 | 4 | 2 | 5 | 3 | 6 | 1 | 4 | 2 | 5 | 2
JMD - C2-STG 1 | STG | 2026-27 | 1 | 1 | 4 | 2 | 5 | 3 | 6 | 1 | 4 | 2 | 7 | 3

## Steam Priority
Asset | Type | Steam Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar
AUXBOIL7_SHP STEAM | AUXBOILER | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
AUXBOIL8_SHP STEAM | AUXBOILER | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
HP Steam PRDS | PRDS | HP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG1_C2_LP STEAM | HRSG | LP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG1_C2_SHP STEAM | HRSG | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG2_C2_LP STEAM | HRSG | LP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG2_C2_SHP STEAM | HRSG | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
LP Steam PRDS | PRDS | LP Steam_Dis | 2026-27 | bar: Apr to Mar
MP Steam PRDS SHP | PRDS | MP Steam_Dis | 2026-27 | bar: Apr to Mar

## Demands
Parameter | Value
MP Steam_Dis | 12542
NITROGEN_ASU | 12747061
LP Steam_Dis | 23081
Utility Water | 1528813
PROCESS FEED WATER | 31711
D M Water | 184969
HP Steam_Dis | -12014
Effluent Treated | 207361
COMPRESSED AIR | 12620018
Power_Dis | 62546650.283
SHP Steam_Dis | 359673
Cooling Water | 100215
Ret steam condensate | -152646
Oxygen | 38907
SWRO WATER | 87646

## Import Power
Source | Capacity MW | Hours | MWh
TOTAL |  |  | 0

## Norms
No data

## U4U Summary
Utility Plant | Utility | UOM | Gen Qty | BPC Gen Qty | Gen Diff % | # Materials | Materials Consumed
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | 3 | SynGas(Unshift), Boiler Feed Water, Power_Dis
Boiler Feed Water | Boiler Feed Water | M3 | 326459.17 | 434662.43 | -24.89 | 3 | D M Water, LP Steam_Dis, Power_Dis
COMPRESED AIR_ASU | COMPRESED AIR_ASU | NM3 | 744489.46 | 731759.52 | 1.74 | 1 | Power_Dis
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14597832.83 | 14348225.29 | 1.74 | 3 | COMPRESED AIR_ASU, COMPRESSED AIR, Power_Dis
Cooling Water | Cooling Water | KM3 | 101091.82 | 105543.15 | -4.22 | 4 | COMPRESSED AIR, Effluent Treated, Power_Dis, SWRO WATER
D M Water | D M Water | M3 | 507320.99 | 604780.6 | -16.11 | 4 | COMPRESSED AIR, NITROGEN_ASU, Power_Dis, SWRO WATER
Effluent Treated | Effluent Treated | M3 | 591509.9 | 608424.78 | -2.78 | 5 | COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
HP Steam PRDS | HP Steam PRDS | MT | 18526.38 | 21910 | -15.44 | 2 | Boiler Feed Water, SHP Steam_Dis
HP Steam_Dis | HP Steam_Dis | MT | 18526.4 | 21909.94 | -15.44 | 1 | HP Steam PRDS
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | 3 | SynGas(Unshift), Boiler Feed Water, Power_Dis
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | 3 | SynGas(Unshift), Boiler Feed Water, Power_Dis
JMD - C2-GTG 1 | POWERGEN | KWH | 74360000 | 75215499.08 | -1.14 | 6 | SynGas(Unshift), COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
JMD - C2-GTG 2 | POWERGEN | KWH | 48280000 | 47632624.3 | 1.36 | 6 | SynGas(Unshift), COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
LP Steam PRDS | LP Steam PRDS | MT | 21642.49 | 25618.73 | -15.52 | 2 | Boiler Feed Water, MP Steam_Dis
LP Steam_Dis | LP Steam_Dis | MT | 58897.89 | 69718.67 | -15.52 | 3 | HRSG1_C2_LP STEAM, HRSG2_C2_LP STEAM, LP Steam PRDS
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 33934.12 | 37693.6 | -9.97 | 2 | Boiler Feed Water, HP Steam_Dis
MP Steam_Dis | MP Steam_Dis | MT | 33934.13 | 37693.55 | -9.97 | 1 | MP Steam PRDS SHP
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13273694.55 | 13335714.29 | -0.47 | 4 | MP Steam_Dis, Power_Dis, Ret steam condensate, Utility Water
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | 4 | MP Steam_Dis, Power_Dis, Ret steam condensate, Utility Water
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | 3 | D M Water, LP Steam_Dis, Power_Dis
SHP Steam_Dis | SHP Steam_Dis | MT | 377013.35 | 380180.38 | -0.83 | 3 | AUXBOIL7_SHP STEAM, HRSG1_C2_SHP STEAM, HRSG2_C2_SHP STEAM
Utility Water | Utility Water | M3 | 1617126.01 | 256859.88 | 529.58 | 2 | COMPRESSED AIR, SWRO WATER
TOTAL |  |  | 155317197.48 | 154319617.05 |  | 68

## U4U Consumption
Utility Plant | Utility | UOM | Gen Qty | BPC Gen Qty | Gen Diff % | Account | Material | Material UOM | Norm | Quantity | BPC Quantity | Qty Diff %
JMD - C2-GTG 1 | POWERGEN | KWH | 74360000 | 75215499.08 | -1.14 | Raw Material | SynGas(Unshift) | MMBTU | 0.004368 | 324804.48 | 328541.3 | -1.14
JMD - C2-GTG 1 | POWERGEN | KWH | 74360000 | 75215499.08 | -1.14 | Utilities | COMPRESSED AIR | NM3 | 0.00128 | 95180.8 | 96268.87 | -1.13
JMD - C2-GTG 1 | POWERGEN | KWH | 74360000 | 75215499.08 | -1.14 | Utilities | Cooling Water | KM3 | 7e-06 | 520.52 | 496.39 | 4.86
JMD - C2-GTG 1 | POWERGEN | KWH | 74360000 | 75215499.08 | -1.14 | Utilities | NITROGEN_ASU | NM3 | 0.00166 | 123437.6 | 124848.69 | -1.13
JMD - C2-GTG 1 | POWERGEN | KWH | 74360000 | 75215499.08 | -1.14 | Utilities | Power_Dis | KWH | 0.00135 | 100386 | 101533.57 | -1.13
JMD - C2-GTG 1 | POWERGEN | KWH | 74360000 | 75215499.08 | -1.14 | Utilities | Utility Water | M3 | 2.3e-05 | 1710.28 | 1744.87 | -1.98
JMD - C2-GTG 2 | POWERGEN | KWH | 48280000 | 47632624.3 | 1.36 | Raw Material | SynGas(Unshift) | MMBTU | 0.004485 | 216535.8 | 213632.32 | 1.36
JMD - C2-GTG 2 | POWERGEN | KWH | 48280000 | 47632624.3 | 1.36 | Utilities | COMPRESSED AIR | NM3 | 0.00128 | 61798.4 | 60970.28 | 1.36
JMD - C2-GTG 2 | POWERGEN | KWH | 48280000 | 47632624.3 | 1.36 | Utilities | Cooling Water | KM3 | 7e-06 | 337.96 | 314.38 | 7.5
JMD - C2-GTG 2 | POWERGEN | KWH | 48280000 | 47632624.3 | 1.36 | Utilities | NITROGEN_ASU | NM3 | 0.00166 | 80144.8 | 79070.84 | 1.36
JMD - C2-GTG 2 | POWERGEN | KWH | 48280000 | 47632624.3 | 1.36 | Utilities | Power_Dis | KWH | 0.00135 | 65178 | 64304.6 | 1.36
JMD - C2-GTG 2 | POWERGEN | KWH | 48280000 | 47632624.3 | 1.36 | Utilities | Utility Water | M3 | 2.3e-05 | 1110.44 | 1105.09 | 0.48
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | Raw Material | SynGas(Unshift) | MMBTU | 2.8762 | 180684.2 | 247872.88 | -27.11
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | Utilities | Boiler Feed Water | M3 | 1.01 | 63448.2 | 87041.85 | -27.11
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 62820 | 86180.05 | -27.11 | Utilities | Power_Dis | KWH | 3.85 | 241857 | 331793.2 | -27.11
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | Raw Material | SynGas(Unshift) | MMBTU | 3.3762 | 365174.55 | 607724.26 | -39.91
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | Utilities | Boiler Feed Water | M3 | 1.16 | 125465.6 | 208800.13 | -39.91
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 108160 | 180000.1 | -39.91 | Utilities | Power_Dis | KWH | 0.285 | 30825.6 | 51300.03 | -39.91
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | Raw Material | SynGas(Unshift) | MMBTU | 3.3575 | 381408.36 | 382750.85 | -0.35
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | Utilities | Boiler Feed Water | M3 | 1.16 | 131776 | 132239.82 | -0.35
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 113600 | 113999.85 | -0.35 | Utilities | Power_Dis | KWH | 0.285 | 32376 | 32489.96 | -0.35
Boiler Feed Water | Boiler Feed Water | M3 | 326459.17 | 434662.43 | -24.89 | Utilities | D M Water | M3 | 0.9 | 293813.25 | 391196.19 | -24.89
Boiler Feed Water | Boiler Feed Water | M3 | 326459.17 | 434662.43 | -24.89 | Utilities | LP Steam_Dis | MT | 0.1 | 32645.92 | 43466.24 | -24.89
Boiler Feed Water | Boiler Feed Water | M3 | 326459.17 | 434662.43 | -24.89 | Utilities | Power_Dis | KWH | 8.1 | 2644319.27 | 3520765.68 | -24.89
COMPRESED AIR_ASU | COMPRESED AIR_ASU | NM3 | 744489.46 | 731759.52 | 1.74 | Utilities | Power_Dis | KWH | 0.125 | 93061.18 | 91469.94 | 1.74
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14597832.83 | 14348225.29 | 1.74 | Utilities | COMPRESED AIR_ASU | NM3 | 0.051 | 744489.47 | 731759.49 | 1.74
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14597832.83 | 14348225.29 | 1.74 | Utilities | COMPRESSED AIR | NM3 | 0.00267 | 38976.21 | 38309.76 | 1.74
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14597832.83 | 14348225.29 | 1.74 | Utilities | Power_Dis | KWH | 0.15 | 2189674.92 | 2152233.79 | 1.74
Cooling Water | Cooling Water | KM3 | 101091.82 | 105543.15 | -4.22 | Utilities | COMPRESSED AIR | NM3 | 0.97474 | 98538.34 | 102877.24 | -4.22
Cooling Water | Cooling Water | KM3 | 101091.82 | 105543.15 | -4.22 | Utilities | Effluent Treated | M3 | 3.8 | 384148.9 | 401063.99 | -4.22
Cooling Water | Cooling Water | KM3 | 101091.82 | 105543.15 | -4.22 | Utilities | Power_Dis | KWH | 210.9 | 21320264.16 | 22259051.62 | -4.22
Cooling Water | Cooling Water | KM3 | 101091.82 | 105543.15 | -4.22 | Utilities | SWRO WATER | M3 | 9.4 | 950263.08 | 992105.67 | -4.22
D M Water | D M Water | M3 | 507320.99 | 604780.6 | -16.11 | Utilities | COMPRESSED AIR | NM3 | 0.04918 | 24950.05 | 29743.11 | -16.11
D M Water | D M Water | M3 | 507320.99 | 604780.6 | -16.11 | Utilities | NITROGEN_ASU | NM3 | 0.63 | 319612.22 | 381011.83 | -16.11
D M Water | D M Water | M3 | 507320.99 | 604780.6 | -16.11 | Utilities | Power_Dis | KWH | 0.92 | 466735.31 | 556398.22 | -16.11
D M Water | D M Water | M3 | 507320.99 | 604780.6 | -16.11 | Utilities | SWRO WATER | M3 | 1.15 | 583419.14 | 695497.78 | -16.11
Effluent Treated | Effluent Treated | M3 | 591509.9 | 608424.78 | -2.78 | Utilities | COMPRESSED AIR | NM3 | 2.2093 | 1306824.01 | 1344194.09 | -2.78
Effluent Treated | Effluent Treated | M3 | 591509.9 | 608424.78 | -2.78 | Utilities | Cooling Water | KM3 | 3.1e-05 | 18.34 | 19.1 | -4
Effluent Treated | Effluent Treated | M3 | 591509.9 | 608424.78 | -2.78 | Utilities | NITROGEN_ASU | NM3 | 0.005814 | 3439.04 | 3537.38 | -2.78
Effluent Treated | Effluent Treated | M3 | 591509.9 | 608424.78 | -2.78 | Utilities | Power_Dis | KWH | 3.2 | 1892831.69 | 1946959.31 | -2.78
Effluent Treated | Effluent Treated | M3 | 591509.9 | 608424.78 | -2.78 | Utilities | Utility Water | M3 | 0.02907 | 17195.19 | 17686.91 | -2.78
HP Steam PRDS | HP Steam PRDS | MT | 18526.38 | 21910 | -15.44 | Utilities | Boiler Feed Water | M3 | 0.064 | 1185.69 | 1402.24 | -15.44
HP Steam PRDS | HP Steam PRDS | MT | 18526.38 | 21910 | -15.44 | Utilities | SHP Steam_Dis | MT | 0.936 | 17340.69 | 20507.71 | -15.44
LP Steam PRDS | LP Steam PRDS | MT | 21642.49 | 25618.73 | -15.52 | Utilities | Boiler Feed Water | M3 | 0.055 | 1190.34 | 1409.03 | -15.52
LP Steam PRDS | LP Steam PRDS | MT | 21642.49 | 25618.73 | -15.52 | Utilities | MP Steam_Dis | MT | 0.945 | 20452.16 | 24209.64 | -15.52
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 33934.12 | 37693.6 | -9.97 | Utilities | Boiler Feed Water | M3 | 0.1 | 3393.41 | 3769.36 | -9.97
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 33934.12 | 37693.6 | -9.97 | Utilities | HP Steam_Dis | MT | 0.9 | 30540.71 | 33924.2 | -9.97
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13273694.55 | 13335714.29 | -0.47 | Utilities | MP Steam_Dis | MT | 2.1e-05 | 278.75 | 280.05 | -0.47
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13273694.55 | 13335714.29 | -0.47 | Utilities | Power_Dis | KWH | 0.47426 | 6295182.38 | 6324508.53 | -0.46
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13273694.55 | 13335714.29 | -0.47 | Utilities | Ret steam condensate | M3 | -1.1e-05 | -146.01 | -146.69 | -0.46
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13273694.55 | 13335714.29 | -0.47 | Utilities | Utility Water | M3 | 0.00154 | 20441.49 | 20536.72 | -0.46
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | MP Steam_Dis | MT | 0.017 | 661.42 | 661.43 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Power_Dis | KWH | 374.61 | 14574951.27 | 14575100.97 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Ret steam condensate | M3 | -0.008 | -311.26 | -311.26 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Utility Water | M3 | 1.23 | 47855.61 | 47856.1 | 0
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | Utilities | D M Water | M3 | 0.9 | 28539.9 | 28540.06 | 0
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | Utilities | LP Steam_Dis | MT | 0.1 | 3171.1 | 3171.12 | 0
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | Utilities | Power_Dis | KWH | 0.631 | 20009.64 | 20009.75 | 0
Utility Water | Utility Water | M3 | 1617126.01 | 256859.88 | 529.58 | Utilities | COMPRESSED AIR | NM3 | 0.21739 | 351547.02 | 55838.77 | 529.58
Utility Water | Utility Water | M3 | 1617126.01 | 256859.88 | 529.58 | Utilities | SWRO WATER | M3 | 1.1 | 1778838.61 | 282545.86 | 529.58
HP Steam_Dis | HP Steam_Dis | MT | 18526.4 | 21909.94 | -15.44 | Utilities | HP Steam PRDS | MT | 1 | 18526.4 | 21909.94 | -15.44
LP Steam_Dis | LP Steam_Dis | MT | 58897.89 | 69718.67 | -15.52 | Utilities | HRSG1_C2_LP STEAM | MT | 0.38727 | 22809.44 | 27000.02 | -15.52
LP Steam_Dis | LP Steam_Dis | MT | 58897.89 | 69718.67 | -15.52 | Utilities | HRSG2_C2_LP STEAM | MT | 0.24527 | 14445.94 | 17099.98 | -15.52
LP Steam_Dis | LP Steam_Dis | MT | 58897.89 | 69718.67 | -15.52 | Utilities | LP Steam PRDS | MT | 0.36746 | 21642.5 | 25618.67 | -15.52
MP Steam_Dis | MP Steam_Dis | MT | 33934.13 | 37693.55 | -9.97 | Utilities | MP Steam PRDS SHP | MT | 1 | 33934.13 | 37693.55 | -9.97
SHP Steam_Dis | SHP Steam_Dis | MT | 377013.35 | 380180.38 | -0.83 | Utilities | AUXBOIL7_SHP STEAM | MT | 0.22668 | 85462.14 | 86180.05 | -0.83
SHP Steam_Dis | SHP Steam_Dis | MT | 377013.35 | 380180.38 | -0.83 | Utilities | HRSG1_C2_SHP STEAM | MT | 0.47346 | 178500.74 | 180000.12 | -0.83
SHP Steam_Dis | SHP Steam_Dis | MT | 377013.35 | 380180.38 | -0.83 | Utilities | HRSG2_C2_SHP STEAM | MT | 0.29986 | 113050.47 | 113999.85 | -0.83