## Plant Info
Field | Value
Plant ID | BA558F95-8A3F-4769-9C78-FF7B6C639DDF
Plant Name | C2 CPP
FY | 2026-27
Month | 4
Year | 2026
Generated | 2026-07-02 15:58:44

## Assets
Asset ID | Asset Name | Display Name | Type | Plant Code | Utility Gen FK | Utility Dist FK
4EA0FA06-25BC-4A96-8279-2F4F4EC52E48 | JMD - C2-GTG 1 | GT-1 | GT | 36H0 | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9
63D052A9-9D13-4C59-B6CD-D26335C94E3B | JMD - C2-GTG 2 | GT-2 | GT | 36GX | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9
8021E7E4-B8FE-41F3-ACAB-F5F139DADBA3 | JMD - C2-STG 1 | STG-1 | STG | 36HM | 0DF562B3-2FE2-4147-AAD1-87332207FB8E | B941711D-5100-499D-A04E-A0EE7C2CF5C9

## Operational Hours
Asset | Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Total
JMD - C2-GTG 1 | GT | 2026-27 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 503 | 8519
JMD - C2-GTG 2 | GT | 2026-27 | 720 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 544 | 8560
JMD - C2-STG 1 | STG | 2026-27 | 0 | 744 | 720 | 744 | 744 | 720 | 744 | 720 | 744 | 744 | 672 | 440 | 7736

## Power Priority
Asset | Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar
JMD - C2-GTG 1 | GT | 2026-27 | 1 | 5 | 5 | 6 | 6 | 1 | 1 | 2 | 2 | 5 | 3 | 3
JMD - C2-GTG 2 | GT | 2026-27 | 1 | 1 | 4 | 2 | 5 | 3 | 6 | 1 | 4 | 2 | 5 | 2
JMD - C2-STG 1 | STG | 2026-27 | 1 | 1 | 4 | 2 | 5 | 3 | 6 | 1 | 4 | 2 | 7 | 3

## Steam Priority
Asset | Type | Steam Type | AOP Year | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar
AUXBOIL7_SHP STEAM | AUXBOILER | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
AUXBOIL8_SHP STEAM | AUXBOILER | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
HP Steam PRDS | PRDS | HP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG1_C2_LP STEAM | HRSG | LP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG1_C2_SHP STEAM | HRSG | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG2_C2_LP STEAM | HRSG | LP Steam_Dis | 2026-27 | bar: Apr to Mar
HRSG2_C2_SHP STEAM | HRSG | SHP Steam_Dis | 2026-27 | bar: Apr to Mar
LP Steam PRDS | PRDS | LP Steam_Dis | 2026-27 | bar: Apr to Mar
MP Steam PRDS SHP | PRDS | MP Steam_Dis | 2026-27 | bar: Apr to Mar

## Demands
Parameter | Value
MP Steam_Dis | 12542
NITROGEN_ASU | 12747061
LP Steam_Dis | 23081
Utility Water | 1528813
PROCESS FEED WATER | 31711
D M Water | 184969
HP Steam_Dis | -12014
Effluent Treated | 207361
COMPRESSED AIR | 12620018
Power_Dis | 62546650.283
SHP Steam_Dis | 359673
Cooling Water | 100215
Ret steam condensate | -152646
Oxygen | 38907
SWRO WATER | 87646

## Import Power
Source | Capacity MW | Hours | MWh
TOTAL |  |  | 0

## Norms
No data

## U4U Summary
Utility Plant | Utility | UOM | Gen Qty | BPC Gen Qty | Gen Diff % | # Materials | Materials Consumed
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 138458.39 | 86180.05 | 60.66 | 3 | SynGas(Unshift), Boiler Feed Water, Power_Dis
Boiler Feed Water | Boiler Feed Water | M3 | 574960.84 | 434662.43 | 32.28 | 3 | D M Water, LP Steam_Dis, Power_Dis
COMPRESED AIR_ASU | COMPRESED AIR_ASU | NM3 | 745122.33 | 731759.52 | 1.83 | 1 | Power_Dis
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14610533.4 | 14348225.29 | 1.83 | 3 | COMPRESED AIR_ASU, COMPRESSED AIR, Power_Dis
Cooling Water | Cooling Water | KM3 | 101100.22 | 105543.15 | -4.21 | 4 | COMPRESSED AIR, Effluent Treated, Power_Dis, SWRO WATER
D M Water | D M Water | M3 | 730973.66 | 604780.6 | 20.87 | 4 | COMPRESSED AIR, NITROGEN_ASU, Power_Dis, SWRO WATER
Effluent Treated | Effluent Treated | M3 | 591541.82 | 608424.78 | -2.77 | 5 | COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
HP Steam PRDS | HP Steam PRDS | MT | 0 | 21910 | -100 | 1 | SHP Steam_Dis
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 180000 | 180000.1 | 0 | 3 | SynGas(Unshift), Boiler Feed Water, Power_Dis
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 195101.61 | 113999.85 | 71.14 | 3 | SynGas(Unshift), Boiler Feed Water, Power_Dis
JMD - C2-GTG 1 | POWERGEN | KWH | 75600000 | 75215499.08 | 0.51 | 6 | SynGas(Unshift), COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
JMD - C2-GTG 2 | POWERGEN | KWH | 48240000 | 47632624.3 | 1.28 | 6 | SynGas(Unshift), COMPRESSED AIR, Cooling Water, NITROGEN_ASU, Power_Dis, Utility Water
LP Steam PRDS | LP Steam PRDS | MT | 0 | 25618.73 | -100 | 1 | MP Steam_Dis
LP Steam_Dis | LP Steam_Dis | MT | 83748.18 | 69718.67 | 20.12 | 3 | HRSG1_C2_LP STEAM, HRSG2_C2_LP STEAM, LP Steam PRDS
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 12542 | 37693.6 | -66.73 | 1 | HP Steam_Dis
MP Steam_Dis | MP Steam_Dis | MT | 13485.16 | 37693.55 | -64.22 | 1 | MP Steam PRDS SHP
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13416588.03 | 13335714.29 | 0.61 | 4 | MP Steam_Dis, Power_Dis, Ret steam condensate, Utility Water
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | 4 | MP Steam_Dis, Power_Dis, Ret steam condensate, Utility Water
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | 3 | D M Water, LP Steam_Dis, Power_Dis
SHP Steam_Dis | SHP Steam_Dis | MT | 359673 | 380180.38 | -5.39 | 3 | AUXBOIL7_SHP STEAM, HRSG1_C2_SHP STEAM, HRSG2_C2_SHP STEAM
Utility Water | Utility Water | M3 | 1617374.4 | 256859.88 | 529.67 | 2 | COMPRESSED AIR, SWRO WATER
TOTAL |  |  | 157281821.04 | 154297707.11 |  | 64

## U4U Consumption
Utility Plant | Utility | UOM | Gen Qty | BPC Gen Qty | Gen Diff % | Account | Material | Material UOM | Norm | Quantity | BPC Quantity | Qty Diff %
JMD - C2-GTG 1 | POWERGEN | KWH | 75600000 | 75215499.08 | 0.51 | Raw Material | SynGas(Unshift) | MMBTU | 0.004368 | 330220.8 | 328541.3 | 0.51
JMD - C2-GTG 1 | POWERGEN | KWH | 75600000 | 75215499.08 | 0.51 | Utilities | COMPRESSED AIR | NM3 | 0.00128 | 96768 | 96268.87 | 0.52
JMD - C2-GTG 1 | POWERGEN | KWH | 75600000 | 75215499.08 | 0.51 | Utilities | Cooling Water | KM3 | 7e-06 | 529.2 | 496.39 | 6.61
JMD - C2-GTG 1 | POWERGEN | KWH | 75600000 | 75215499.08 | 0.51 | Utilities | NITROGEN_ASU | NM3 | 0.00166 | 125496 | 124848.69 | 0.52
JMD - C2-GTG 1 | POWERGEN | KWH | 75600000 | 75215499.08 | 0.51 | Utilities | Power_Dis | KWH | 0.00135 | 102060 | 101533.57 | 0.52
JMD - C2-GTG 1 | POWERGEN | KWH | 75600000 | 75215499.08 | 0.51 | Utilities | Utility Water | M3 | 2.3e-05 | 1738.8 | 1744.87 | -0.35
JMD - C2-GTG 2 | POWERGEN | KWH | 48240000 | 47632624.3 | 1.28 | Raw Material | SynGas(Unshift) | MMBTU | 0.004485 | 216356.4 | 213632.32 | 1.28
JMD - C2-GTG 2 | POWERGEN | KWH | 48240000 | 47632624.3 | 1.28 | Utilities | COMPRESSED AIR | NM3 | 0.00128 | 61747.2 | 60970.28 | 1.27
JMD - C2-GTG 2 | POWERGEN | KWH | 48240000 | 47632624.3 | 1.28 | Utilities | Cooling Water | KM3 | 7e-06 | 337.68 | 314.38 | 7.41
JMD - C2-GTG 2 | POWERGEN | KWH | 48240000 | 47632624.3 | 1.28 | Utilities | NITROGEN_ASU | NM3 | 0.00166 | 80078.4 | 79070.84 | 1.27
JMD - C2-GTG 2 | POWERGEN | KWH | 48240000 | 47632624.3 | 1.28 | Utilities | Power_Dis | KWH | 0.00135 | 65124 | 64304.6 | 1.27
JMD - C2-GTG 2 | POWERGEN | KWH | 48240000 | 47632624.3 | 1.28 | Utilities | Utility Water | M3 | 2.3e-05 | 1109.52 | 1105.09 | 0.4
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 138458.39 | 86180.05 | 60.66 | Raw Material | SynGas(Unshift) | MMBTU | 2.8762 | 398236.93 | 247872.88 | 60.66
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 138458.39 | 86180.05 | 60.66 | Utilities | Boiler Feed Water | M3 | 1.01 | 139842.97 | 87041.85 | 60.66
AUXBOIL7_SHP STEAM | AUXBOIL7_SHP STEAM | MT | 138458.39 | 86180.05 | 60.66 | Utilities | Power_Dis | KWH | 3.85 | 533064.8 | 331793.2 | 60.66
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 180000 | 180000.1 | 0 | Raw Material | SynGas(Unshift) | MMBTU | 3.3762 | 607723.92 | 607724.26 | 0
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 180000 | 180000.1 | 0 | Utilities | Boiler Feed Water | M3 | 1.16 | 208800 | 208800.13 | 0
HRSG1_C2_SHP STEAM | HRSG1_C2_SHP STEAM | MT | 180000 | 180000.1 | 0 | Utilities | Power_Dis | KWH | 0.285 | 51300 | 51300.03 | 0
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 195101.61 | 113999.85 | 71.14 | Raw Material | SynGas(Unshift) | MMBTU | 3.3575 | 655047.41 | 382750.85 | 71.14
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 195101.61 | 113999.85 | 71.14 | Utilities | Boiler Feed Water | M3 | 1.16 | 226317.87 | 132239.82 | 71.14
HRSG2_C2_SHP STEAM | HRSG2_C2_SHP STEAM | MT | 195101.61 | 113999.85 | 71.14 | Utilities | Power_Dis | KWH | 0.285 | 55603.96 | 32489.96 | 71.14
Boiler Feed Water | Boiler Feed Water | M3 | 574960.84 | 434662.43 | 32.28 | Utilities | D M Water | M3 | 0.9 | 517464.76 | 391196.19 | 32.28
Boiler Feed Water | Boiler Feed Water | M3 | 574960.84 | 434662.43 | 32.28 | Utilities | LP Steam_Dis | MT | 0.1 | 57496.08 | 43466.24 | 32.28
Boiler Feed Water | Boiler Feed Water | M3 | 574960.84 | 434662.43 | 32.28 | Utilities | Power_Dis | KWH | 8.1 | 4657182.82 | 3520765.68 | 32.28
COMPRESED AIR_ASU | COMPRESED AIR_ASU | NM3 | 745122.33 | 731759.52 | 1.83 | Utilities | Power_Dis | KWH | 0.125 | 93140.29 | 91469.94 | 1.83
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14610533.4 | 14348225.29 | 1.83 | Utilities | COMPRESED AIR_ASU | NM3 | 0.051 | 745137.2 | 731759.49 | 1.83
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14610533.4 | 14348225.29 | 1.83 | Utilities | COMPRESSED AIR | NM3 | 0.00267 | 39010.12 | 38309.76 | 1.83
COMPRESSED AIR | COMPRESSED AIR | NM3 | 14610533.4 | 14348225.29 | 1.83 | Utilities | Power_Dis | KWH | 0.15 | 2191580.01 | 2152233.79 | 1.83
Cooling Water | Cooling Water | KM3 | 101100.22 | 105543.15 | -4.21 | Utilities | COMPRESSED AIR | NM3 | 0.97474 | 98546.53 | 102877.24 | -4.21
Cooling Water | Cooling Water | KM3 | 101100.22 | 105543.15 | -4.21 | Utilities | Effluent Treated | M3 | 3.8 | 384180.83 | 401063.99 | -4.21
Cooling Water | Cooling Water | KM3 | 101100.22 | 105543.15 | -4.21 | Utilities | Power_Dis | KWH | 210.9 | 21322035.93 | 22259051.62 | -4.21
Cooling Water | Cooling Water | KM3 | 101100.22 | 105543.15 | -4.21 | Utilities | SWRO WATER | M3 | 9.4 | 950342.05 | 992105.67 | -4.21
D M Water | D M Water | M3 | 730973.66 | 604780.6 | 20.87 | Utilities | COMPRESSED AIR | NM3 | 0.04918 | 35949.28 | 29743.11 | 20.87
D M Water | D M Water | M3 | 730973.66 | 604780.6 | 20.87 | Utilities | NITROGEN_ASU | NM3 | 0.63 | 460513.4 | 381011.83 | 20.87
D M Water | D M Water | M3 | 730973.66 | 604780.6 | 20.87 | Utilities | Power_Dis | KWH | 0.92 | 672495.76 | 556398.22 | 20.87
D M Water | D M Water | M3 | 730973.66 | 604780.6 | 20.87 | Utilities | SWRO WATER | M3 | 1.15 | 840619.71 | 695497.78 | 20.87
Effluent Treated | Effluent Treated | M3 | 591541.82 | 608424.78 | -2.77 | Utilities | COMPRESSED AIR | NM3 | 2.2093 | 1306894.52 | 1344194.09 | -2.77
Effluent Treated | Effluent Treated | M3 | 591541.82 | 608424.78 | -2.77 | Utilities | Cooling Water | KM3 | 3.1e-05 | 18.34 | 19.1 | -3.99
Effluent Treated | Effluent Treated | M3 | 591541.82 | 608424.78 | -2.77 | Utilities | NITROGEN_ASU | NM3 | 0.005814 | 3439.22 | 3537.38 | -2.77
Effluent Treated | Effluent Treated | M3 | 591541.82 | 608424.78 | -2.77 | Utilities | Power_Dis | KWH | 3.2 | 1892933.82 | 1946959.31 | -2.77
Effluent Treated | Effluent Treated | M3 | 591541.82 | 608424.78 | -2.77 | Utilities | Utility Water | M3 | 0.02907 | 17196.12 | 17686.91 | -2.77
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13416588.03 | 13335714.29 | 0.61 | Utilities | MP Steam_Dis | MT | 2.1e-05 | 281.75 | 280.05 | 0.61
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13416588.03 | 13335714.29 | 0.61 | Utilities | Power_Dis | KWH | 0.47426 | 6362951.04 | 6324508.53 | 0.61
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13416588.03 | 13335714.29 | 0.61 | Utilities | Ret steam condensate | M3 | -1.1e-05 | -147.58 | -146.69 | 0.61
NITROGEN_ASU | NITROGEN_ASU | NM3 | 13416588.03 | 13335714.29 | 0.61 | Utilities | Utility Water | M3 | 0.00154 | 20661.55 | 20536.72 | 0.61
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | MP Steam_Dis | MT | 0.017 | 661.42 | 661.43 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Power_Dis | KWH | 374.61 | 14574951.27 | 14575100.97 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Ret steam condensate | M3 | -0.008 | -311.26 | -311.26 | 0
Oxygen | Oxygen | MT | 38907 | 38907.65 | 0 | Utilities | Utility Water | M3 | 1.23 | 47855.61 | 47856.1 | 0
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | Utilities | D M Water | M3 | 0.9 | 28539.9 | 28540.06 | 0
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | Utilities | LP Steam_Dis | MT | 0.1 | 3171.1 | 3171.12 | 0
PROCESS FEED WATER | PROCESS FEED WATER | M3 | 31711 | 31711.18 | 0 | Utilities | Power_Dis | KWH | 0.631 | 20009.64 | 20009.75 | 0
Utility Water | Utility Water | M3 | 1617374.4 | 256859.88 | 529.67 | Utilities | COMPRESSED AIR | NM3 | 0.21739 | 351601.02 | 55838.77 | 529.67
Utility Water | Utility Water | M3 | 1617374.4 | 256859.88 | 529.67 | Utilities | SWRO WATER | M3 | 1.1 | 1779111.84 | 282545.86 | 529.67
LP Steam_Dis | LP Steam_Dis | MT | 83748.18 | 69718.67 | 20.12 | Utilities | HRSG1_C2_LP STEAM | MT | 0.38727 | 32433.24 | 27000.02 | 20.12
LP Steam_Dis | LP Steam_Dis | MT | 83748.18 | 69718.67 | 20.12 | Utilities | HRSG2_C2_LP STEAM | MT | 0.24527 | 20541 | 17099.98 | 20.12
LP Steam_Dis | LP Steam_Dis | MT | 83748.18 | 69718.67 | 20.12 | Utilities | LP Steam PRDS | MT | 0.36746 | 30773.94 | 25618.67 | 20.12
MP Steam_Dis | MP Steam_Dis | MT | 13485.16 | 37693.55 | -64.22 | Utilities | MP Steam PRDS SHP | MT | 1 | 13485.16 | 37693.55 | -64.22
SHP Steam_Dis | SHP Steam_Dis | MT | 359673 | 380180.38 | -5.39 | Utilities | AUXBOIL7_SHP STEAM | MT | 0.22668 | 81531.39 | 86180.05 | -5.39
SHP Steam_Dis | SHP Steam_Dis | MT | 359673 | 380180.38 | -5.39 | Utilities | HRSG1_C2_SHP STEAM | MT | 0.47346 | 170290.78 | 180000.12 | -5.39
SHP Steam_Dis | SHP Steam_Dis | MT | 359673 | 380180.38 | -5.39 | Utilities | HRSG2_C2_SHP STEAM | MT | 0.29986 | 107850.83 | 113999.85 | -5.39
LP Steam PRDS | LP Steam PRDS | MT | 0 | 25618.73 | -100 | Utilities | MP Steam_Dis | MT | 0.945 | 0 | 24209.64 | -100
MP Steam PRDS SHP | MP Steam PRDS SHP | MT | 12542 | 37693.6 | -66.73 | Utilities | HP Steam_Dis | MT | 0.9 | 11287.8 | 33924.2 | -66.73
HP Steam PRDS | HP Steam PRDS | MT | 0 | 21910 | -100 | Utilities | SHP Steam_Dis | MT | 0.936 | 0 | 20507.71 | -100