## Scenarios
SHP Steam DTA-DTA PCG-SEZ PCG
Minimum flow requirement is from DTA to DTA PCG & DTA PCG to SEZ PCG or vice-versa is 50 TPH.
Deficit of DTA PCG or SEZ PCG will met by DTA CPP & Surplus steam of DTA PCG will be supplied to DTA.
Transfer Combinations & Scenarios are as follows:
DTA -> | DTA PCG |  | 36BK -> | 36KO
DTA -> | SEZ PCG |  | 36BK -> | 36KQ
DTA PCG -> | DTA |  | 36KO -> | 36BK
Scenario-1 : DTA PCG in deficit of SHP Steam then DTA CPP will supply steam to DTA PCG
| DTA |  |  |  | DTA
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| HRSG | (12*110) | 931 |  | PRDS - HHP to HP | 5
| HRSG (Fr9) | (1*275) | 260 |  | Extraction STG | 1271
| AB | (6*110) | 417 |  | DTA PCG | 232
[5 empty] | SEZ PCG | 100
| Generation |  | 1608 |  | Consumption | 1608
| DTA PCG |  |  |  | DTA PCG
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| Superheaters |  | 540 |  | Air Separation Unit | 700
| HRSG (Fr9) | (2*165) | 0 |  | PRDS | 29
| DTA CPP |  | 232 |  | Process Units | 43
| Generation |  | 772 |  | Consumption | 772
| SEZ PCG |  |  |  | SEZ PCG
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| Superheaters |  | 657 |  | Air Separation Unit | 700
| SNG Unit |  | 60 |  | PRDS | 74
| DTA CPP |  | 100 |  | Process Units | 43
| Generation |  | 817 |  | Consumption | 817
Scenario-2 : With Operation of 1 DTA PCG GT/HRSG, DTA PCG will be self sufficient / minimum import from DTA CPP. Also need to consider minimum transfer flow requirement between DTA CPP & DTA PCG.
| DTA |  |  |  | DTA
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| HRSG | (12*110) | 876 |  | PRDS - HHP to HP | 5
| HRSG (Fr9) | (1*275) | 260 |  | Extraction STG | 1271
| AB | (6*110) | 270 |  | DTA PCG | 70
| DTA PCG |  | 0 |  | SEZ PCG | 60
| Generation |  | 1406 |  | Consumption | 1406
| DTA PCG |  |  |  | DTA PCG
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| Superheaters |  | 540 |  | Air Separation Unit | 703
| HRSG (Fr9) | (2*165) | 165 |  | PRDS | 29
| DTA CPP |  | 70 |  | Process Units | 43
[5 empty] | DTA CPP | 0
| Generation |  | 775 |  | Consumption | 775
| SEZ PCG |  |  |  | SEZ PCG
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| Superheaters |  | 657 |  | Air Separation Unit | 700
| SNG Unit |  | 100 |  | PRDS | 74
| DTA CPP |  | 60 |  | Process Units | 43
| Generation |  | 817 |  | Consumption | 817
Scenario-3 : With Operation of both DTA PCG GTs/HRSGs, DTA PCG will start export steam to DTA CPP. Hence, In DTA CPP operation optimised by minimum AB (4 out of 6) at turndown loading and reducing fired steam from HRSGs sequentially.
| DTA |  |  |  | DTA
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| HRSG | (12*110) | 770 |  | PRDS - HHP to HP | 5
| HRSG (Fr9) | (1*275) | 260 |  | Extraction STG | 1270
| AB | (6*110) | 205 |  | DTA PCG | 0
| DTA PCG CPP |  | 100 |  | SEZ PCG | 60
| Generation |  | 1335 |  | Consumption | 1335
| DTA PCG |  |  |  | DTA PCG
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| Superheaters |  | 540 |  | Air Separation Unit | 700
| HRSG (Fr9) | (2*165) | 332 |  | PRDS | 29
| DTA CPP |  | 0 |  | Process Units | 43
[5 empty] | DTA CPP | 100
| Generation |  | 872 |  | Consumption | 872
| SEZ PCG |  |  |  | SEZ PCG
| Equipment | Op. Capacity | TPH |  | Demand from | TPH
| Superheaters |  | 757 |  | Air Separation Unit | 700
| SNG Unit |  | 0 |  | PRDS | 74
| DTA CPP |  | 60 |  | Process Units | 43
| Generation |  | 817 |  | Consumption | 817

## Sheet1 (hidden)
SHP Steam DTA to DTA PCG
Scenario-1 : DTA PCG in deficit of SHP Steam
| Generation |  |  | Consumption
| DTA |  |  | DTA
| Equipment | Capacity | TPH | Demand from | TPH
| HRSG | (12*110) | 870 | PRDS - HHP to HP | 5
| HRSG (Fr9) | (1*275) | 260 | Extraction STG | 1271
| AB | (6*110) | 317 | DTA PCG & SEZ PCG | 171
| Generation |  | 1447 | Consumption | 1447
| Generation |  |  | Consumption
| DTA PCG |  |  | DTA PCG
| Equipment | Capacity | TPH | Demand from | TPH
| Superheaters |  | 540 | Air Separation Unit | 700
| HRSG (Fr9) | (2*184) | 0 | PRDS | 29
| DTA CPP |  | 171 | Process Units | 43
| SEZ PCG |  | 75 | SEZ PCG | 14
| Generation |  | 786 | Consumption | 786
| Generation |  |  | Consumption
| SEZ PCG |  |  | SEZ PCG
| Equipment | Capacity | TPH | Demand from | TPH
| Superheaters |  | 757 | Air Separation Unit | 700
| SNG Unit |  | 121 | PRDS | 74
| DTA PCG |  | 14 | Process Units | 43
|  |  |  | DTA PCG | 75
| Generation |  | 892 | Consumption | 892